## Sheet1
Aug, 2011 Beowawe Binary Bottoming Cycle Data - DE-EE0002856
Date | Time | Gen. Output [MW] | Parasitic [MW] | Net | T Dry Bulb [F] | Wet Bulb Temp [F] | Brine Exit Temp [F] | Brine Flow [gpm] | Brine Inlet Temp [F] | Cooling Water Inlet Temp [F] | Cooling Water Outlet Temp [F]
Aug 1, 2011 | 2401:00
Aug 1, 2011 | 2402:00 | 0.557 | 0.27405 | 0.28295 | 62.9 | 58 | 128 | 1149.8335 | 209 | 73 | 85
Aug 1, 2011 | 2403:00
Aug 1, 2011 | 2404:00 | 0.587 | 0.27405 | 0.31295 | 61.6 | 58 | 128 | 1184.8335 | 209 | 73 | 84
Aug 1, 2011 | 2405:00
Aug 1, 2011 | 2406:00 | 0.69 | 0.27405 | 0.41595 | 62 | 58 | 129 | 1305.0002 | 209 | 71 | 83
Aug 1, 2011 | 2407:00
Aug 1, 2011 | 2408:00 | 0.69 | 0.27405 | 0.41595 | 65 | 61 | 129 | 1305.0002 | 209 | 72 | 84
Aug 1, 2011 | 2409:00
Aug 1, 2011 | 2410:00 | 0.749 | 0.27405 | 0.47495 | Not Recorded | Not Recorded | Not Recorded | 1373.8336 | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2411:00
Aug 1, 2011 | 2412:00 | 0 | 0 | 0 | 88 | 68 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2413:00
Aug 1, 2011 | 2414:00 | 0.563 | 0.27405 | 0.28895 | 92 | 70 | Not Recorded | 1156.8335 | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2415:00
Aug 1, 2011 | 2416:00 | 0 | 0 | 0 | 87 | 70 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2417:00
Aug 1, 2011 | 2418:00 | 0 | 0 | 0 | 82 | 68 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2419:00
Aug 1, 2011 | 2420:00 | 0 | 0 | 0 | 78 | 66 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2421:00
Aug 1, 2011 | 2422:00 | 0 | 0 | 0 | 76 | 61 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 1, 2011 | 2423:00
Aug 2, 2011 | 2400:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2401:00
Aug 2, 2011 | 2402:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2403:00
Aug 2, 2011 | 2404:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2405:00
Aug 2, 2011 | 2406:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2407:00
Aug 2, 2011 | 2408:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2409:00
Aug 2, 2011 | 2410:00 | 0.48 | 0.11318 | 0.36682 | Not Recorded | Not Recorded | Not Recorded | 1060.0002 | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2411:00
Aug 2, 2011 | 2412:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2413:00
Aug 2, 2011 | 2414:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2415:00
Aug 2, 2011 | 2416:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2417:00
Aug 2, 2011 | 2418:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2419:00
Aug 2, 2011 | 2420:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 2, 2011 | 2421:00
Aug 2, 2011 | 2422:00 | 0 | 0 | 0 | 62.3 | 56 | 130 |  | 210 | 65 | 68
Aug 2, 2011 | 2423:00
Aug 3, 2011 | 2400:00 | 0.807 | 0.27583 | 0.53117 | 60.1 | 54 | 130 | 1441.5003 | 209 | 70 | 83
Aug 3, 2011 | 2401:00
Aug 3, 2011 | 2402:00 | 0.913 | 0.27583 | 0.63717 | 57 | 52 | 132 | 1565.167 | 209 | 69 | 82
Aug 3, 2011 | 2403:00
Aug 3, 2011 | 2404:00 | 1.031 | 0.27583 | 0.75517 | 53.3 | 50 | 135 | 1702.8337 | 209 | 68 | 81
Aug 3, 2011 | 2405:00
Aug 3, 2011 | 2406:00 | 1.131 | 0.27583 | 0.85517 | 63.7 | 52 | 134 | 1819.5004 | 209 | 68 | 81
Aug 3, 2011 | 2407:00
Aug 3, 2011 | 2408:00 | 0.672 | 0.27583 | 0.39617 | 75 | 62 | 129 | 1284.0002 | 209 | 71 | 83
Aug 3, 2011 | 2409:00
Aug 3, 2011 | 2410:00 | 0 | 0 | 0 | 80 | 67 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2411:00
Aug 3, 2011 | 2412:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2413:00
Aug 3, 2011 | 2414:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2415:00
Aug 3, 2011 | 2416:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2417:00
Aug 3, 2011 | 2418:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2419:00
Aug 3, 2011 | 2420:00 | 0 | 0 | 0 | 81.4 | 66 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2421:00
Aug 3, 2011 | 2422:00 | 0 | 0 | 0 | 71.3 | 65 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 3, 2011 | 2423:00
Aug 4, 2011 | 2400:00 | 0 | 0 | 0 | 66.8 | 62 | 137 |  | 209 | 67 | 78
Aug 4, 2011 | 2401:00
Aug 4, 2011 | 2402:00 | 0.786 | 0.32395 | 0.46205 | 60.5 | 58 | 130 | 1417.0003 | 209 | 70 | 82
Aug 4, 2011 | 2403:00
Aug 4, 2011 | 2404:00 | 0.901 | 0.32395 | 0.57705 | 59.4 | 54 | 133 | 1551.167 | 209 | 69 | 81
Aug 4, 2011 | 2405:00
Aug 4, 2011 | 2406:00 | 0.933 | 0.32395 | 0.60905 | 59.2 | 54 | 132 | 1588.5003 | 209 | 69 | 81
Aug 4, 2011 | 2407:00
Aug 4, 2011 | 2408:00 | 0 | 0 | 0 | 80.3 | 65.8 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2409:00
Aug 4, 2011 | 2410:00 | 0 | 0 | 0 | 85.9 | 70.4 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2411:00
Aug 4, 2011 | 2412:00 | 0 | 0 | 0 | 90.2 | 71.2 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2413:00
Aug 4, 2011 | 2414:00 | 0 | 0 | 0 | 94.2 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2415:00
Aug 4, 2011 | 2416:00 | 0 | 0 | 0 | 92.5 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2417:00
Aug 4, 2011 | 2418:00 | 0 | 0 | 0 | 89 | 70.2 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 4, 2011 | 2419:00
Aug 4, 2011 | 2420:00 | 0.773 | 0.32395 | 0.44905 | 81.4 | 65 | 130 | 1401.8336 | 209 | 68 | 80
Aug 4, 2011 | 2421:00
Aug 4, 2011 | 2422:00 | 0.719 | 0.32395 | 0.39505 | 70.7 | 62 | 129 | 1338.8336 | 209 | 69 | 81
Aug 4, 2011 | 2423:00
Aug 5, 2011 | 2400:00 | 0.875 | 0.39792 | 0.47708 | 63.7 | 56 | 132 | 1520.8336 | 209 | 68 | 80
Aug 5, 2011 | 2401:00
Aug 5, 2011 | 2402:00 | 1.106 | 0.39792 | 0.70808 | 61 | 53 | 136 | 1790.3337 | 209 | 66 | 80
Aug 5, 2011 | 2403:00
Aug 5, 2011 | 2404:00 | 1.091 | 0.39792 | 0.69308 | 57.6 | 50 | 135 | 1772.8337 | 209 | 65 | 78
Aug 5, 2011 | 2405:00
Aug 5, 2011 | 2406:00 | 1.125 | 0.39792 | 0.72708 | 57.6 | 48 | 136 | 1812.5004 | 209 | 65 | 78
Aug 5, 2011 | 2407:00
Aug 5, 2011 | 2408:00 | 0.899 | 0.39792 | 0.50108 | 75.2 | 62.8 | 133 | 1548.8336 | 209 | 68 | 81
Aug 5, 2011 | 2409:00
Aug 5, 2011 | 2410:00 | 0 | 0 | 0 | 81.7 | 65.2 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 5, 2011 | 2411:00
Aug 5, 2011 | 2412:00 | 0 | 0 | 0 | 88.1 | 68 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 5, 2011 | 2413:00
Aug 5, 2011 | 2414:00 | 0 | 0 | 0 | 91.3 | 73 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 5, 2011 | 2415:00
Aug 5, 2011 | 2416:00 | 0 | 0 | 0 | 92.9 | 74 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 5, 2011 | 2417:00
Aug 5, 2011 | 2418:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 5, 2011 | 2419:00
Aug 5, 2011 | 2420:00 | 0.63 | 0.39792 | 0.23208 | 77.9 | 64 | 128 | 1235.0002 | 209 | 69 | 81
Aug 5, 2011 | 2421:00
Aug 5, 2011 | 2422:00 | 0.778 | 0.39792 | 0.38008 | 73.3 | 62 | 130 | 1407.6669 | 209 | 68 | 80
Aug 5, 2011 | 2423:00
Aug 6, 2011 | 2400:00 | 0.94 | 0.35212 | 0.58788 | 67.9 | 56 | 133 | 1596.667 | 209 | 67 | 79
Aug 6, 2011 | 2401:00
Aug 6, 2011 | 2402:00 | 1.046 | 0.35212 | 0.69388 | 63 | 54 | 134 | 1720.3337 | 209 | 65 | 78
Aug 6, 2011 | 2403:00
Aug 6, 2011 | 2404:00 | 0.956 | 0.35212 | 0.60388 | 63 | 55 | 133 | 1615.3337 | 209 | 67 | 79
Aug 6, 2011 | 2405:00
Aug 6, 2011 | 2406:00 | 1.153 | 0.35212 | 0.80088 | 58.7 | 54 | 136 | 1845.1671 | 209 | 65 | 78
Aug 6, 2011 | 2407:00
Aug 6, 2011 | 2408:00 | 0.779 | 0.35212 | 0.42688 | 76 | 62 | 132 | 1408.8336 | 209 | 68 | 81
Aug 6, 2011 | 2409:00
Aug 6, 2011 | 2410:00 | 0.71 | 0.35212 | 0.35788 | 88 | 68 | 133 | 1328.3336 | 209 | 70 | 82
Aug 6, 2011 | 2411:00
Aug 6, 2011 | 2412:00 | 0 | 0 | 0 | 95 | 70 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2413:00
Aug 6, 2011 | 2414:00 | 0 | 0 | 0 | 96 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2415:00
Aug 6, 2011 | 2416:00 | 0 | 0 | 0 | 96 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2417:00
Aug 6, 2011 | 2418:00 | 0 | 0 | 0 | 93 | 73 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2419:00
Aug 6, 2011 | 2420:00 | 0 | 0 | 0 | 85.3 | 69 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2421:00
Aug 6, 2011 | 2422:00 | 0 | 0 | 0 | 77.8 | 62 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 6, 2011 | 2423:00
Aug 7, 2011 | 2400:00 | 1.049 | 0.38768 | 0.66132 | 78.3 | 65 | 140 | 1723.8337 | 209 | 68 | 84
Aug 7, 2011 | 2401:00
Aug 7, 2011 | 2402:00 | 0 | 0 | 0 | 74.2 | 63 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2403:00
Aug 7, 2011 | 2404:00 | 0.88 | 0.38768 | 0.49232 | 68.9 | 58 | 141 | 1526.667 | 209 | 67 | 79
Aug 7, 2011 | 2405:00
Aug 7, 2011 | 2406:00 | 1.22 | 0.38768 | 0.83232 | 62.8 | 55 | 149 | 1923.3337 | 209 | 67 | 80
Aug 7, 2011 | 2407:00
Aug 7, 2011 | 2408:00 | 0.911 | 0.38768 | 0.52332 | 73 | 63 | 144 | 1562.8336 | 209 | 68 | 80
Aug 7, 2011 | 2409:00
Aug 7, 2011 | 2410:00 | 0 | 0 | 0 | 86 | 67 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2411:00
Aug 7, 2011 | 2412:00 | 0 | 0 | 0 | 90 | 71 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2413:00
Aug 7, 2011 | 2414:00 | 0 | 0 | 0 | 96 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2415:00
Aug 7, 2011 | 2416:00 | 0 | 0 | 0 | 94 | 72 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2417:00
Aug 7, 2011 | 2418:00 | 0 | 0 | 0 | 88 | 71 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 7, 2011 | 2419:00
Aug 7, 2011 | 2420:00 | 0.82 | 0.38768 | 0.43232 | 79.9 | 62 | 132 | 1456.6669 | 209 | 66 | 78
Aug 7, 2011 | 2421:00
Aug 7, 2011 | 2422:00 | 0.984 | 0.38768 | 0.59632 | 71.8 | 56 | 136 | 1648.0003 | 209 | 65 | 77
Aug 7, 2011 | 2423:00
Aug 8, 2011 | 2400:00 | 1.049 | 0.64167 | 0.40733 | 68.8 | 56 | 138 | 1723.8337 | 209 | 65 | 77
Aug 8, 2011 | 2401:00
Aug 8, 2011 | 2402:00 | 1.132 | 0.64167 | 0.49033 | 61.4 | 49 | 139 | 1820.667 | 209 | 63 | 75
Aug 8, 2011 | 2403:00
Aug 8, 2011 | 2404:00 | 1.373 | 0.64167 | 0.73133 | 56.3 | 48 | 142 | 2101.8338 | 209 | 61 | 74
Aug 8, 2011 | 2405:00
Aug 8, 2011 | 2406:00 | 1.422 | 0.64167 | 0.78033 | 54.9 | 44 | 144 | 2159.0005 | 209 | 61 | 74
Aug 8, 2011 | 2407:00
Aug 8, 2011 | 2408:00 | 1.207 | 0.64167 | 0.56533 | 70 | 56 | 143 | 1908.1671 | 209 | 64 | 77
Aug 8, 2011 | 2409:00
Aug 8, 2011 | 2410:00 | 0.957 | 0.64167 | 0.31533 | Not Recorded | Not Recorded | Not Recorded | 1616.5003 | Not Recorded | Not Recorded | Not Recorded
Aug 8, 2011 | 2411:00
Aug 8, 2011 | 2412:00 | 0.83 | 0.64167 | 0.18833 | 94 | 67 | 135 | 1468.3336 | 209 | 69 | 81
Aug 8, 2011 | 2413:00
Aug 8, 2011 | 2414:00 | 0.752 | 0.64167 | 0.11033 | Not Recorded | Not Recorded | Not Recorded | 1377.3336 | Not Recorded | Not Recorded | Not Recorded
Aug 8, 2011 | 2415:00
Aug 8, 2011 | 2416:00 | 0.711 | 0.64167 | 0.06933 | Not Recorded | Not Recorded | Not Recorded | 1329.5002 | Not Recorded | Not Recorded | Not Recorded
Aug 8, 2011 | 2417:00
Aug 8, 2011 | 2418:00 | 0.765 | 0.64167 | 0.12333 | 88 | 65 | 134 | 1392.5003 | 209 | 69 | 81
Aug 8, 2011 | 2419:00
Aug 8, 2011 | 2420:00 | 0.848 | 0.64167 | 0.20633 | 80.8 | 62 | 134 | 1489.3336 | 209 | 67 | 79
Aug 8, 2011 | 2421:00
Aug 8, 2011 | 2422:00 | 8.991 | 0.64167 | 8.3493 | 71.3 | 59 | 135 | 10989.503 | 209 | 66 | 78
Aug 8, 2011 | 2423:00
Aug 9, 2011 | 2400:00 | 1.024 | 0.64167 | 0.38233 | 65.5 | 51 | 136 | 1694.667 | 209 | 63 | 75
Aug 9, 2011 | 2401:00
Aug 9, 2011 | 2402:00 | 1.157 | 0.64167 | 0.51533 | 65.9 | 54 | 140 | 1849.8337 | 209 | 63 | 76
Aug 9, 2011 | 2403:00
Aug 9, 2011 | 2404:00 | 1.26 | 0.64167 | 0.61833 | 57.8 | 48 | 139 | 1970.0004 | 209 | 62 | 75
Aug 9, 2011 | 2405:00
Aug 9, 2011 | 2406:00 | 1.251 | 0.64167 | 0.60933 | 57.8 | 48 | 140 | 1959.5004 | 209 | 63 | 76
Aug 9, 2011 | 2407:00
Aug 9, 2011 | 2408:00 | 1.198 | 0.64167 | 0.55633 | 77 | 64 | 140 | 1897.6671 | 209 | 65 | 78
Aug 9, 2011 | 2409:00
Aug 9, 2011 | 2410:00 | 0.901 | 0.64167 | 0.25933 | 82 | 64 | 138 | 1551.167 | 209 | 68 | 80
Aug 9, 2011 | 2411:00
Aug 9, 2011 | 2412:00 | 0.756 | 0.64167 | 0.11433 | Not Recorded | Not Recorded | Not Recorded | 1382.0003 | Not Recorded | Not Recorded | Not Recorded
Aug 9, 2011 | 2413:00
Aug 9, 2011 | 2414:00 | 0.759 | 0.64167 | 0.11733 | 94.3 | 68.6 | 134 | 1385.5003 | 209 | 70 | 81
Aug 9, 2011 | 2415:00
Aug 9, 2011 | 2416:00 | 0.702 | 0.64167 | 0.06033 | Not Recorded | Not Recorded | Not Recorded | 1319.0002 | Not Recorded | Not Recorded | Not Recorded
Aug 9, 2011 | 2417:00
Aug 9, 2011 | 2418:00 | 0.807 | 0.64167 | 0.16533 | 87 | 69 | 136 | 1441.5003 | 209 | 69 | 81
Aug 9, 2011 | 2419:00
Aug 9, 2011 | 2420:00 | 0.815 | 0.64167 | 0.17333 | 77.4 | 61 | 136 | 1450.8336 | 209 | 68 | 80
Aug 9, 2011 | 2421:00
Aug 9, 2011 | 2422:00 | 0.881 | 0.64167 | 0.23933 | 71.8 | 57 | 136 | 1527.8336 | 209 | 66 | 77
Aug 9, 2011 | 2423:00
Aug 10, 2011 | 2400:00 | 0.983 | 0.64167 | 0.34133 | 64.4 | 53 | 137 | 1646.8337 | 209 | 65 | 77
Aug 10, 2011 | 2401:00
Aug 10, 2011 | 2402:00 | 1.2 | 0.64167 | 0.55833 | 62.5 | 50 | 139 | 1900.0004 | 209 | 63 | 76
Aug 10, 2011 | 2403:00
Aug 10, 2011 | 2404:00 | 1.421 | 0.64167 | 0.77933 | 55.1 | 45 | 141 | 2157.8338 | 209 | 61 | 75
Aug 10, 2011 | 2405:00
Aug 10, 2011 | 2406:00 | 1.456 | 0.64167 | 0.81433 | 52.6 | 46 | 143 | 2198.6672 | 209 | 62 | 75
Aug 10, 2011 | 2407:00
Aug 10, 2011 | 2408:00 | 1.136 | 0.64167 | 0.49433 | 77 | 59 | 140 | 1825.3337 | 209 | 64 | 77
Aug 10, 2011 | 2409:00
Aug 10, 2011 | 2410:00 | 0.958 | 0.64167 | 0.31633 | Not Recorded | Not Recorded | Not Recorded | 1617.667 | Not Recorded | Not Recorded | Not Recorded
Aug 10, 2011 | 2411:00
Aug 10, 2011 | 2412:00 | 0.726 | 0.64167 | 0.08433 | Not Recorded | Not Recorded | Not Recorded | 1347.0002 | Not Recorded | Not Recorded | Not Recorded
Aug 10, 2011 | 2413:00
Aug 10, 2011 | 2414:00 | 0.706 | 0.64167 | 0.06433 | 95 | 69 | Not Recorded | 1323.6669 | Not Recorded | Not Recorded | Not Recorded
Aug 10, 2011 | 2415:00
Aug 10, 2011 | 2416:00 | 0.672 | 0.64167 | 0.03033 | Not Recorded | Not Recorded | Not Recorded | 1284.0002 | Not Recorded | Not Recorded | Not Recorded
Aug 10, 2011 | 2417:00
Aug 10, 2011 | 2418:00 | 0.69 | 0.64167 | 0.04833 | 88 | 68 | 133 | 1305.0002 | 209 | 69 | 81
Aug 10, 2011 | 2419:00
Aug 10, 2011 | 2420:00 | 0.76 | 0.64167 | 0.11833 | 81.9 | 67 | 133 | 1386.6669 | 209 | 68 | 80
Aug 10, 2011 | 2421:00
Aug 10, 2011 | 2422:00 | 0.924 | 0.64167 | 0.28233 | 72.4 | 60 | 135 | 1578.0003 | 208 | 67 | 79
Aug 10, 2011 | 2423:00
Aug 11, 2011 | 2400:00 | 0.978 | 0.64167 | 0.33633 | 70.4 | 57 | 136 | 1641.0003 | 209 | 66 | 78
Aug 11, 2011 | 2401:00
Aug 11, 2011 | 2402:00 | 1.08 | 0.64167 | 0.43833 | 67.8 | 57 | 137 | 1760.0004 | 208 | 66 | 79
Aug 11, 2011 | 2403:00
Aug 11, 2011 | 2404:00 | 1.11 | 0.64167 | 0.46833 | 65.9 | 54 | 137 | 1795.0004 | 209 | 65 | 78
Aug 11, 2011 | 2405:00
Aug 11, 2011 | 2406:00 | 1.222 | 0.64167 | 0.58033 | 60.7 | 51 | 141 | 1925.6671 | 209 | 65 | 78
Aug 11, 2011 | 2407:00
Aug 11, 2011 | 2408:00 | 1.14 | 0.64167 | 0.49833 | 78 | 65 | 138 | 1830.0004 | 209 | 67 | 79
Aug 11, 2011 | 2409:00
Aug 11, 2011 | 2410:00 | 0.859 | 0.64167 | 0.21733 | 88 | 65 | 134 | 1502.167 | 209 | 69 | 80
Aug 11, 2011 | 2411:00
Aug 11, 2011 | 2412:00 | 0.689 | 0.64167 | 0.04733 | 93 | 69 | 133 | 1303.8336 | 209 | 70 | 81
Aug 11, 2011 | 2413:00
Aug 11, 2011 | 2414:00 | 0.668 | 0.64167 | 0.02633 | 94 | 63 | 132 | 1279.3336 | 209 | 69 | 81
Aug 11, 2011 | 2415:00
Aug 11, 2011 | 2416:00 | 0.67 | 0.64167 | 0.02833 | 93.1 | 62 | 132 | 1281.6669 | 209 | 70 | 81
Aug 11, 2011 | 2417:00
Aug 11, 2011 | 2418:00 | 0.638 | 0.64167 | -0.00367 | 88 | 62 | 132 | 1244.3335 | 209 | 70 | 81
Aug 11, 2011 | 2419:00
Aug 11, 2011 | 2420:00 | 0.765 | 0.64167 | 0.12333 | 75 | 61 | 135 | 1392.5003 | 209 | 67 | 79
Aug 11, 2011 | 2421:00
Aug 11, 2011 | 2422:00 | 1.02 | 0.64167 | 0.37833 | 69 | 56 | 136 | 1690.0003 | 209 | 66 | 78
Aug 11, 2011 | 2423:00
Aug 12, 2011 | 2400:00 | 1.163 | 0.54809 | 0.61491 | 65 | 52 | 140 | 1856.8337 | 209 | 65 | 77
Aug 12, 2011 | 2401:00
Aug 12, 2011 | 2402:00 | 1.239 | 0.54809 | 0.69091 | 60 | 46 | 141 | 1945.5004 | 209 | 64 | 77
Aug 12, 2011 | 2403:00
Aug 12, 2011 | 2404:00 | 1.305 | 0.54809 | 0.75691 | 59 | 45 | 142 | 2022.5004 | 209 | 64 | 77
Aug 12, 2011 | 2405:00
Aug 12, 2011 | 2406:00 | 1.259 | 0.54809 | 0.71091 | 57 | 44 | 142 | 1968.8338 | 209 | 63 | 76
Aug 12, 2011 | 2407:00
Aug 12, 2011 | 2408:00 | 1.006 | 0.54809 | 0.45791 | 83.7 | 54 | 138 | 1673.667 | 209 | 67 | 79
Aug 12, 2011 | 2409:00
Aug 12, 2011 | 2410:00 | 0.801 | 0.54809 | 0.25291 | 87.1 | 60 | 134 | 1434.5003 | 209 | 69 | 81
Aug 12, 2011 | 2411:00
Aug 12, 2011 | 2412:00 | 0.609 | 0.54809 | 0.060907 | 95 | 62 | 130 | 1210.5002 | 209 | 71 | 82
Aug 12, 2011 | 2413:00
Aug 12, 2011 | 2414:00 | 0.601 | 0.54809 | 0.052907 | 96 | 62 | 131 | 1201.1669 | 209 | 70 | 82
Aug 12, 2011 | 2415:00
Aug 12, 2011 | 2416:00 | 0.561 | 0.54809 | 0.012907 | 97 | 64 | 131 | 1154.5002 | 209 | 71 | 82
Aug 12, 2011 | 2417:00
Aug 12, 2011 | 2418:00 | 0 | 0 | 0 | 93 | 62 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 12, 2011 | 2419:00
Aug 12, 2011 | 2420:00 | 0 | 0 | 0 | 86 | 69 | 138 |  | 209 | 67 | 79
Aug 12, 2011 | 2421:00
Aug 12, 2011 | 2422:00 | 0.93 | 0.54809 | 0.38191 | 75 | 54 | 137 | 1585.0003 | 209 | 67 | 79
Aug 12, 2011 | 2423:00
Aug 13, 2011 | 2400:00 | 1.011 | 0.64167 | 0.36933 | 71 | 52 | 137 | 1679.5003 | 209 | 67 | 79
Aug 13, 2011 | 2401:00
Aug 13, 2011 | 2402:00 | 1.189 | 0.64167 | 0.54733 | 63 | 49 | 140 | 1887.1671 | 209 | 64 | 77
Aug 13, 2011 | 2403:00
Aug 13, 2011 | 2404:00 | 1.325 | 0.64167 | 0.68333 | 63 | 48 | 143 | 2045.8338 | 209 | 65 | 78
Aug 13, 2011 | 2405:00
Aug 13, 2011 | 2406:00 | 1.348 | 0.64167 | 0.70633 | 59 | 42 | 141 | 2072.6671 | 209 | 63 | 76
Aug 13, 2011 | 2407:00
Aug 13, 2011 | 2408:00 | 1.083 | 0.64167 | 0.44133 | 81 | 57 | 138 | 1763.5004 | 209 | 67 | 79
Aug 13, 2011 | 2409:00
Aug 13, 2011 | 2410:00 | 0.828 | 0.64167 | 0.18633 | 91.4 | 60 | 134 | 1466.0003 | 209 | 69 | 80
Aug 13, 2011 | 2411:00
Aug 13, 2011 | 2412:00 | 0.704 | 0.64167 | 0.06233 | 91 | 57 | 132 | 1321.3336 | 209 | 69 | 80
Aug 13, 2011 | 2413:00
Aug 13, 2011 | 2414:00 | 0.734 | 0.64167 | 0.09233 | 88.2 | 57 | 133 | 1356.3336 | 209 | 69 | 80
Aug 13, 2011 | 2415:00
Aug 13, 2011 | 2416:00 | 0.721 | 0.64167 | 0.07933 | 85 | 60 | 133 | 1341.1669 | 209 | 69 | 81
Aug 13, 2011 | 2417:00
Aug 13, 2011 | 2418:00 | 0.806 | 0.64167 | 0.16433 | 84.2 | 64 | 133 | 1440.3336 | 209 | 68 | 80
Aug 13, 2011 | 2419:00
Aug 13, 2011 | 2420:00 | 1.023 | 0.64167 | 0.38133 | 67 | 55 | 137 | 1693.5003 | 209 | 65 | 77
Aug 13, 2011 | 2421:00
Aug 13, 2011 | 2422:00 | 1.192 | 0.64167 | 0.55033 | 65 | 48 | 139 | 1890.6671 | 209 | 64 | 77
Aug 13, 2011 | 2423:00
Aug 14, 2011 | 2400:00 | 1.159 | 0.64167 | 0.51733 | 64 | 48 | 141 | 1852.1671 | 209 | 65 | 77
Aug 14, 2011 | 2401:00
Aug 14, 2011 | 2402:00 | 1.463 | 0.64167 | 0.82133 | 56 | 44 | 143 | 2206.8338 | 209 | 62 | 76
Aug 14, 2011 | 2403:00
Aug 14, 2011 | 2404:00 | 1.555 | 0.64167 | 0.91333 | 50 | 39 | 145 | 2314.1672 | 209 | 61 | 75
Aug 14, 2011 | 2405:00
Aug 14, 2011 | 2406:00 | 1.608 | 0.64167 | 0.96633 | 54 | 39 | 144 | 2376.0005 | 209 | 61 | 74
Aug 14, 2011 | 2407:00
Aug 14, 2011 | 2408:00 | 1.255 | 0.64167 | 0.61333 | 71 | 50 | 142 | 1964.1671 | 209 | 64 | 77
Aug 14, 2011 | 2409:00
Aug 14, 2011 | 2410:00 | 0.947 | 0.64167 | 0.30533 | 85 | 58 | 137 | 1604.8336 | 209 | 67 | 79
Aug 14, 2011 | 2411:00
Aug 14, 2011 | 2412:00 | 0.566 | 0.64167 | -0.07567 | 96.3 | 62 | 134 | 1160.3335 | 209 | 70 | 81
Aug 14, 2011 | 2413:00
Aug 14, 2011 | 2414:00 | 0.537 | 0.64167 | -0.10467 | 94 | 64 | 130 | 1126.5002 | 209 | 71 | 81
Aug 14, 2011 | 2415:00
Aug 14, 2011 | 2416:00 | 0.516 | 0.64167 | -0.12567 | 91.3 | 63 | 130 | 1102.0002 | 209 | 71 | 82
Aug 14, 2011 | 2417:00
Aug 14, 2011 | 2418:00 | 0.486 | 0.64167 | -0.15567 | 88.7 | 65 | 130 | 1067.0002 | 209 | 71 | 82
Aug 14, 2011 | 2419:00
Aug 14, 2011 | 2420:00 | 0.469 | 0.64167 | -0.17267 | 85 | 63 | 130 | 1047.1668 | 209 | 71 | 82
Aug 14, 2011 | 2421:00
Aug 14, 2011 | 2422:00 | 0.936 | 0.64167 | 0.29433 | 76 | 54 | 137 | 1592.0003 | 209 | 67 | 79
Aug 14, 2011 | 2423:00
Aug 15, 2011 | 2400:00 | 1.059 | 0.35381 | 0.70519 | 72 | 53 | 139 | 1735.5004 | 209 | 66 | 78
Aug 15, 2011 | 2401:00
Aug 15, 2011 | 2402:00 | 0.936 | 0.35381 | 0.58219 | 65 | 49 | 139 | 1592.0003 | 209 | 65 | 77
Aug 15, 2011 | 2403:00
Aug 15, 2011 | 2404:00 | 1.214 | 0.35381 | 0.86019 | 63 | 49 | 140 | 1916.3337 | 209 | 65 | 78
Aug 15, 2011 | 2405:00
Aug 15, 2011 | 2406:00 | 1.187 | 0.35381 | 0.83319 | 64 | 49 | 140 | 1884.8337 | 209 | 65 | 78
Aug 15, 2011 | 2407:00
Aug 15, 2011 | 2408:00 | 1.079 | 0.35381 | 0.72519 | 78 | 55 | 138 | 1758.8337 | 209 | 67 | 79
Aug 15, 2011 | 2409:00
Aug 15, 2011 | 2410:00 | 0.947 | 0.35381 | 0.59319 | 85.3 | 57 | 136 | 1604.8336 | 209 | 67 | 79
Aug 15, 2011 | 2411:00
Aug 15, 2011 | 2412:00 | 0.566 | 0.35381 | 0.21219 | 86.2 | 58 | 136 | 1160.3335 | 209 | 68 | 80
Aug 15, 2011 | 2413:00
Aug 15, 2011 | 2414:00 | 0 | 0 | 0 | 87 | 58 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 15, 2011 | 2415:00
Aug 15, 2011 | 2416:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 15, 2011 | 2417:00
Aug 15, 2011 | 2418:00 | 0 | 0 | 0 | 83.2 | 57 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 15, 2011 | 2419:00
Aug 15, 2011 | 2420:00 | 0 | 0 | 0 | 69 | 54 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 15, 2011 | 2421:00
Aug 15, 2011 | 2422:00 | 0 | 0 | 0 | 65 | 48 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 15, 2011 | 2423:00
Aug 16, 2011 | 2400:00 | 0 | 0 | 0 | 62 | 44 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2401:00
Aug 16, 2011 | 2402:00 | 0 | 0 | 0 | 58 | 44 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2403:00
Aug 16, 2011 | 2404:00 | 0 | 0 | 0 | 56 | 43 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2405:00
Aug 16, 2011 | 2406:00 | 0 | 0 | 0 | 58 | 47 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2407:00
Aug 16, 2011 | 2408:00 | 0 | 0 | 0 | 75.6 | 54 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2409:00
Aug 16, 2011 | 2410:00 | 0 | 0 | 0 | 82.8 | 58 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2411:00
Aug 16, 2011 | 2412:00 | 0 | 0 | 0 | 87 | 60 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2413:00
Aug 16, 2011 | 2414:00 | 0 | 0 | 0 | 90 | 61 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2415:00
Aug 16, 2011 | 2416:00 | 0 | 0 | 0 | 91.5 | 62 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2417:00
Aug 16, 2011 | 2418:00 | 0 | 0 | 0 | 87.8 | 62 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2419:00
Aug 16, 2011 | 2420:00 | 0 | 0 | 0 | 75 | 56 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2421:00
Aug 16, 2011 | 2422:00 | 0 | 0 | 0 | 72 | 53 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 16, 2011 | 2423:00
Aug 16, 2011 | 2400:00 | 0 | 0 | 0 | 69 | 52 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2401:00
Aug 17, 2011 | 2402:00 | 0 | 0 | 0 | 61 | 45 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2403:00
Aug 17, 2011 | 2404:00 | 0 | 0 | 0 | 57 | 43 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2405:00
Aug 17, 2011 | 2406:00 | 0 | 0 | 0 | 55 | 42 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2407:00
Aug 17, 2011 | 2408:00 | 0 | 0 | 0 | 76 | 55 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2409:00
Aug 17, 2011 | 2410:00 | 0 | 0 | 0 | 85.5 | 60 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2411:00
Aug 17, 2011 | 2412:00 | 0 | 0 | 0 | 93.6 | 60 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2413:00
Aug 17, 2011 | 2414:00 | 0 | 0 | 0 | 99 | 63 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2415:00
Aug 17, 2011 | 2416:00 | 0 | 0 | 0 | 93.1 | 64 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2417:00
Aug 17, 2011 | 2418:00 | 0 | 0 | 0 | 88.7 | 61 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2419:00
Aug 17, 2011 | 2420:00 | 0 | 0 | 0 | 78 | 57 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2421:00
Aug 17, 2011 | 2422:00 | 0 | 0 | 0 | 74 | 50 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 17, 2011 | 2423:00
Aug 18, 2011 | 2400:00 | 0 | 0 | 0 | 68 | 50 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2401:00
Aug 18, 2011 | 2402:00 | 0 | 0 | 0 | 60 | 42 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2403:00
Aug 18, 2011 | 2404:00 | 0 | 0 | 0 | 56 | 42 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2405:00
Aug 18, 2011 | 2406:00 | 0 | 0 | 0 | 56 | 42 | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2407:00
Aug 18, 2011 | 2408:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2409:00
Aug 18, 2011 | 2410:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2411:00
Aug 18, 2011 | 2412:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2413:00
Aug 18, 2011 | 2414:00 | 0 | 0 | 0 | Not Recorded | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2415:00
Aug 18, 2011 | 2416:00 | 0 | 0 | 0 | 94.5 | Not Recorded | Not Recorded |  | Not Recorded | Not Recorded | Not Recorded
Aug 18, 2011 | 2417:00
Aug 18, 2011 | 2418:00 | 1.257 | 0.17833 | 1.0787 | 91.3 | 76.1 | 149 | 1966.5004 | 209 | 72 | 85
Aug 18, 2011 | 2419:00
Aug 18, 2011 | 2420:00 | 1.813 | 0.17833 | 1.6347 | 78 | 58 | 149 | 2615.1673 | 209 | 68 | 82
Aug 18, 2011 | 2421:00
Aug 18, 2011 | 2422:00 | 2.296 | 0.17833 | 2.1177 | 70 | 56 | 150 | 3178.6674 | 209 | 69 | 84
Aug 18, 2011 | 2423:00
Aug 19, 2011 | 2400:00 | 2.441 | 0.61173 | 1.8293 | 63 | 50 | 152 | 3347.8341 | 209 | 67 | 82
Aug 19, 2011 | 2401:00
Aug 19, 2011 | 2402:00 | 2.518 | 0.61173 | 1.9063 | 61 | 48 | 152 | 3437.6675 | 209 | 66 | 81
Aug 19, 2011 | 2403:00
Aug 19, 2011 | 2404:00 | 2.469 | 0.61173 | 1.8573 | 61 | 48 | 152 | 3380.5008 | 209 | 66 | 82
Aug 19, 2011 | 2405:00
Aug 19, 2011 | 2406:00 | 2.512 | 0.61173 | 1.9003 | 57 | 46 | 151 | 3430.6675 | 209 | 65 | 81
Aug 19, 2011 | 2407:00
Aug 19, 2011 | 2408:00 | 2.35 | 0.61173 | 1.7383 | 73.8 | 57.1 | 152 | 3241.6674 | 209 | 70 | 85
Aug 19, 2011 | 2409:00
Aug 19, 2011 | 2410:00 | 2.173 | 0.61173 | 1.5613 | 83.5 | 62.9 | 153 | 3035.1674 | 209 | 73 | 88
Aug 19, 2011 | 2411:00
Aug 19, 2011 | 2412:00 | 2.022 | 0.61173 | 1.4103 | 90 | 66 | 152 | 2859.0007 | 209 | 74 | 89
Aug 19, 2011 | 2413:00
Aug 19, 2011 | 2414:00 | 1.92 | 0.61173 | 1.3083 | 91.8 | 68 | 152 | 2740.0006 | 209 | 74 | 89
Aug 19, 2011 | 2415:00
Aug 19, 2011 | 2416:00 | 1.447 | 0.61173 | 0.83527 | 95.2 | 65 | Not Recorded | 2188.1671 | Not Recorded | Not Recorded | Not Recorded
Aug 19, 2011 | 2417:00
Aug 19, 2011 | 2418:00 | 1.92 | 0.61173 | 1.3083 | 91.9 | 65 | 151 | 2740.0006 | 209 | 75 | 89
Aug 19, 2011 | 2419:00
Aug 19, 2011 | 2420:00 | 0.907 | 0.61173 | 0.29527 | 78 | 60 | 143 | 1558.167 | 209 | 68 | 78
Aug 19, 2011 | 2421:00
Aug 19, 2011 | 2422:00 | 2.203 | 0.61173 | 1.5913 | 74 | 57 | 151 | 3070.1674 | 209 | 70 | 85
Aug 19, 2011 | 2423:00
Aug 20, 2011 | 2400:00 | 2.33 | 0.64167 | 1.6883 | 69 | 54 | 152 | 3218.3341 | 209 | 69 | 84
Aug 20, 2011 | 2401:00
Aug 20, 2011 | 2402:00 | 2.298 | 0.64167 | 1.6563 | 71 | 57 | 152 | 3181.0008 | 209 | 70 | 85
Aug 20, 2011 | 2403:00
Aug 20, 2011 | 2404:00 | 2.426 | 0.64167 | 1.7843 | 58 | 47 | 152 | 3330.3341 | 209 | 67 | 82
Aug 20, 2011 | 2405:00
Aug 20, 2011 | 2406:00 | 2.481 | 0.64167 | 1.8393 | 60 | 48 | 152 | 3394.5008 | 209 | 66 | 81
Aug 20, 2011 | 2407:00
Aug 20, 2011 | 2408:00 | 2.271 | 0.64167 | 1.6293 | 77.2 | 57 | 153 | 3149.5008 | 209 | 70 | 85
Aug 20, 2011 | 2409:00
Aug 20, 2011 | 2410:00 | 2.091 | 0.64167 | 1.4493 | 88.4 | 61 | 151 | 2939.5007 | 209 | 72 | 87
Aug 20, 2011 | 2411:00
Aug 20, 2011 | 2412:00 | 1.998 | 0.64167 | 1.3563 | 97.7 | 63 | 149 | 2831.0007 | 209 | 73 | 87
Aug 20, 2011 | 2413:00
Aug 20, 2011 | 2414:00 | 1.967 | 0.64167 | 1.3253 | 97 | 71 | 150 | 2794.834 | 209 | 73 | 88
Aug 20, 2011 | 2415:00
Aug 20, 2011 | 2416:00 | 1.968 | 0.64167 | 1.3263 | 94 | 65 | 150 | 2796.0007 | 209 | 74 | 88
Aug 20, 2011 | 2417:00
Aug 20, 2011 | 2418:00 | 1.64 | 0.64167 | 0.99833 | 93.1 | 65 | 147 | 2413.3339 | 209 | 76 | 89
Aug 20, 2011 | 2419:00
Aug 20, 2011 | 2420:00 | 2.103 | 0.64167 | 1.4613 | 80 | 60 | 148 | 2953.5007 | 209 | 72 | 86
Aug 20, 2011 | 2421:00
Aug 20, 2011 | 2422:00 | 2.304 | 0.64167 | 1.6623 | 70 | 54 | 152 | 3188.0008 | 209 | 70 | 85
Aug 20, 2011 | 2423:00
Aug 21, 2011 | 2400:00 | 2.246 | 0.64167 | 1.6043 | 80 | 60 | 153 | 3120.3341 | 209 | 70 | 86
Aug 21, 2011 | 2401:00
Aug 21, 2011 | 2402:00 | 2.284 | 0.64167 | 1.6423 | 79 | 64 | 153 | 3164.6674 | 209 | 70 | 85
Aug 21, 2011 | 2403:00
Aug 21, 2011 | 2404:00 | 2.345 | 0.64167 | 1.7033 | 70 | 56 | 152 | 3235.8341 | 209 | 68 | 84
Aug 21, 2011 | 2405:00
Aug 21, 2011 | 2406:00 | 2.49 | 0.64167 | 1.8483 | 60 | 48 | 152 | 3405.0008 | 209 | 65 | 81
Aug 21, 2011 | 2407:00
Aug 21, 2011 | 2408:00 | 2.417 | 0.64167 | 1.7753 | 77.9 | 55 | 152 | 3319.8341 | 209 | 68 | 83
Aug 21, 2011 | 2409:00
Aug 21, 2011 | 2410:00 | 2.244 | 0.64167 | 1.6023 | 88.9 | 60 | 153 | 3118.0007 | 209 | 71 | 86
Aug 21, 2011 | 2411:00
Aug 21, 2011 | 2412:00 | 2.146 | 0.64167 | 1.5043 | 97 | 61 | 152 | 3003.6674 | 209 | 72 | 87
Aug 21, 2011 | 2413:00
Aug 21, 2011 | 2414:00 | 2 | 0.64167 | 1.3583 | 95.6 | 65 | 150 | 2833.334 | 209 | 73 | 87
Aug 21, 2011 | 2415:00
Aug 21, 2011 | 2416:00 | 1.918 | 0.64167 | 1.2763 | 96.3 | 66 | 148 | 2737.6673 | 209 | 73 | 88
Aug 21, 2011 | 2417:00
Aug 21, 2011 | 2418:00 | 1.898 | 0.64167 | 1.2563 | 92 | 64 | 149 | 2714.334 | 209 | 74 | 88
Aug 21, 2011 | 2419:00
Aug 21, 2011 | 2420:00 | 2.198 | 0.64167 | 1.5563 | 76 | 60 | 152 | 3064.3341 | 209 | 70 | 85
Aug 21, 2011 | 2421:00
Aug 21, 2011 | 2422:00 | 2.216 | 0.64167 | 1.5743 | 75 | 59 | 153 | 3085.3341 | 209 | 70 | 86
Aug 21, 2011 | 2423:00
Aug 22, 2011 | 2400:00 | 2.411 | 0.64167 | 1.7693 | 70 | 55 | 152 | 3312.8341 | 209 | 69 | 84
Aug 22, 2011 | 2401:00
Aug 22, 2011 | 2402:00 | 2.452 | 0.64167 | 1.8103 | 63 | 51 | 152 | 3360.6675 | 209 | 65 | 81
Aug 22, 2011 | 2403:00
Aug 22, 2011 | 2404:00 | 2.471 | 0.64167 | 1.8293 | 55 | 45 | 152 | 3382.8342 | 209 | 65 | 80
Aug 22, 2011 | 2405:00
Aug 22, 2011 | 2406:00 | 2.524 | 0.64167 | 1.8823 | 53 | 43 | 152 | 3444.6675 | 209 | 63 | 78
Aug 22, 2011 | 2407:00
Aug 22, 2011 | 2408:00 | 2.347 | 0.64167 | 1.7053 | 72.9 | 54 | 152 | 3238.1674 | 209 | 68 | 83
Aug 22, 2011 | 2409:00
Aug 22, 2011 | 2410:00 | 2.273 | 0.64167 | 1.6313 | 85.1 | 62 | 153 | 3151.8341 | 209 | 71 | 86
Aug 22, 2011 | 2411:00
Aug 22, 2011 | 2412:00 | 2.13 | 0.64167 | 1.4883 | 94.5 | 61 | 151 | 2985.0007 | 209 | 73 | 88
Aug 22, 2011 | 2413:00
Aug 22, 2011 | 2414:00 | 2 | 0.64167 | 1.3583 | 95.8 | 63 | 151 | 2833.334 | 209 | 73 | 87
Aug 22, 2011 | 2415:00
Aug 22, 2011 | 2416:00 | 2.001 | 0.64167 | 1.3593 | 91.4 | 64 | 151 | 2834.5007 | 209 | 73 | 87
Aug 22, 2011 | 2417:00
Aug 22, 2011 | 2418:00 | 1.993 | 0.64167 | 1.3513 | 88.6 | 63 | 150 | 2825.1673 | 209 | 73 | 88
Aug 22, 2011 | 2419:00
Aug 22, 2011 | 2420:00 | 2.163 | 0.64167 | 1.5213 | 83 | 65 | 153 | 3023.5007 | 209 | 71 | 86
Aug 22, 2011 | 2421:00
Aug 22, 2011 | 2422:00 | 2.256 | 0.64167 | 1.6143 | 76 | 60 | 153 | 3132.0008 | 209 | 70 | 85
Aug 22, 2011 | 2423:00
Aug 23, 2011 | 2400:00 | 2.257 | 0.64167 | 1.6153 | 75 | 59 | 153 | 3133.1674 | 209 | 70 | 85
Aug 23, 2011 | 2401:00
Aug 23, 2011 | 2402:00 | 2.327 | 0.64167 | 1.6853 | 65 | 52 | 152 | 3214.8341 | 209 | 67 | 83
Aug 23, 2011 | 2403:00
Aug 23, 2011 | 2404:00 | 2.421 | 0.64167 | 1.7793 | 61 | 48 | 152 | 3324.5008 | 209 | 66 | 82
Aug 23, 2011 | 2405:00
Aug 23, 2011 | 2406:00 | 2.556 | 0.64167 | 1.9143 | 56 | 45 | 152 | 3482.0009 | 209 | 64 | 79
Aug 23, 2011 | 2407:00
Aug 23, 2011 | 2408:00 | 2.344 | 0.64167 | 1.7023 | 75.6 | 54 | 152 | 3234.6674 | 209 | 68 | 83
Aug 23, 2011 | 2409:00
Aug 23, 2011 | 2410:00 | 2.216 | 0.64167 | 1.5743 | 87.1 | 65 | 153 | 3085.3341 | 209 | 71 | 86
Aug 23, 2011 | 2411:00
Aug 23, 2011 | 2412:00 | 2.021 | 0.64167 | 1.3793 | 98.1 | 66 | 151 | 2857.834 | 209 | 73 | 88
Aug 23, 2011 | 2413:00
Aug 23, 2011 | 2414:00 | 1.838 | 0.64167 | 1.1963 | 96.5 | 67 | 148 | 2644.3339 | 209 | 74 | 88
Aug 23, 2011 | 2415:00
Aug 23, 2011 | 2416:00 | 1.712 | 0.64167 | 1.0703 | 96.5 | 68 | 148 | 2497.3339 | 209 | 75 | 89
Aug 23, 2011 | 2417:00
Aug 23, 2011 | 2418:00 | 1.77 | 0.64167 | 1.1283 | 93.8 | 67 | 147 | 2565.0006 | 209 | 74 | 88
Aug 23, 2011 | 2419:00
Aug 23, 2011 | 2420:00 | 2.072 | 0.64167 | 1.4303 | 82 | 62 | 151 | 2917.334 | 209 | 72 | 87
Aug 23, 2011 | 2421:00
Aug 23, 2011 | 2422:00 | 2.153 | 0.64167 | 1.5113 | 76 | 58 | 153 | 3011.8341 | 209 | 71 | 86
Aug 23, 2011 | 2423:00
Aug 24, 2011 | 2400:00 | 2.183 | 0.64167 | 1.5413 | 76 | 58 | 153 | 3046.8341 | 209 | 72 | 87
Aug 24, 2011 | 2401:00
Aug 24, 2011 | 2402:00 | 2.302 | 0.64167 | 1.6603 | 68 | 53 | 153 | 3185.6674 | 209 | 69 | 84
Aug 24, 2011 | 2403:00
Aug 24, 2011 | 2404:00 | 2.384 | 0.64167 | 1.7423 | 65 | 51 | 153 | 3281.3341 | 209 | 69 | 84
Aug 24, 2011 | 2405:00
Aug 24, 2011 | 2406:00 | 2.28 | 0.64167 | 1.6383 | 61 | 49 | 153 | 3160.0008 | 209 | 69 | 84
Aug 24, 2011 | 2407:00
Aug 24, 2011 | 2408:00 | 2.178 | 0.64167 | 1.5363 | 80 | 60 | 153 | 3041.0007 | 209 | 72 | 87
Aug 24, 2011 | 2409:00
Aug 24, 2011 | 2410:00 | 1.976 | 0.64167 | 1.3343 | 90 | 64 | 150 | 2805.334 | 209 | 73 | 88
Aug 24, 2011 | 2411:00
Aug 24, 2011 | 2412:00 | 1.796 | 0.64167 | 1.1543 | 98 | 68 | 147 | 2595.3339 | 209 | 74 | 88
Aug 24, 2011 | 2413:00
Aug 24, 2011 | 2414:00 | 1.709 | 0.64167 | 1.0673 | 102 | 70 | 146 | 2493.8339 | 209 | 75 | 89
Aug 24, 2011 | 2415:00
Aug 24, 2011 | 2416:00 | 1.644 | 0.64167 | 1.0023 | 99 | 78 | Not Recorded | 2418.0005 | Not Recorded | Not Recorded | Not Recorded
Aug 24, 2011 | 2417:00
Aug 24, 2011 | 2418:00 | 1.6 | 0.64167 | 0.95833 | 93 | 77 | Not Recorded | 2366.6672 | Not Recorded | Not Recorded | Not Recorded
Aug 24, 2011 | 2419:00
Aug 24, 2011 | 2420:00 | 1.837 | 0.64167 | 1.1953 | 89 | 66 | 148 | 2643.1673 | 209 | 74 | 88
Aug 24, 2011 | 2421:00
Aug 24, 2011 | 2422:00 | 1.994 | 0.64167 | 1.3523 | 79 | 60 | 150 | 2826.334 | 209 | 72 | 87
Aug 24, 2011 | 2423:00
Aug 25, 2011 | 2400:00 | 2.116 | 0.62385 | 1.4922 | 78 | 60 | 153 | 2968.6674 | 209 | 72 | 87
Aug 25, 2011 | 2401:00
Aug 25, 2011 | 2402:00 | 2.118 | 0.62385 | 1.4942 | 77 | 59 | 154 | 2971.0007 | 209 | 72 | 87
Aug 25, 2011 | 2403:00
Aug 25, 2011 | 2404:00 | 2.135 | 0.62385 | 1.5112 | 68 | 54 | 152 | 2990.834 | 209 | 70 | 85
Aug 25, 2011 | 2405:00
Aug 25, 2011 | 2406:00 | 2.208 | 0.62385 | 1.5842 | 67 | 53 | 153 | 3076.0007 | 209 | 69 | 84
Aug 25, 2011 | 2407:00
Aug 25, 2011 | 2408:00 | 2.208 | 0.62385 | 1.5842 | 76 | 58 | 154 | 3076.0007 | 209 | 72 | 87
Aug 25, 2011 | 2409:00
Aug 25, 2011 | 2410:00 | 1.305 | 0.62385 | 0.68115 | 97 | 65 | 153 | 2022.5004 | 209 | 74 | 88
Aug 25, 2011 | 2411:00
Aug 25, 2011 | 2412:00 | 1.75 | 0.62385 | 1.1262 | 100 | 68 | 153 | 2541.6672 | 209 | 75 | 89
Aug 25, 2011 | 2413:00
Aug 25, 2011 | 2414:00 | 1.65 | 0.62385 | 1.0262 | 101 | 69 | 150 | 2425.0005 | 209 | 76 | 89
Aug 25, 2011 | 2415:00
Aug 25, 2011 | 2416:00 | 1.6 | 0.62385 | 0.97615 | 100 | 69 | 151 | 2366.6672 | 209 | 75 | 89
Aug 25, 2011 | 2417:00
Aug 25, 2011 | 2418:00 | 1.525 | 0.62385 | 0.90115 | 94 | 69 | 150 | 2279.1672 | 209 | 75 | 88
Aug 25, 2011 | 2419:00
Aug 25, 2011 | 2420:00 | 1.824 | 0.62385 | 1.2002 | 82 | 62 | 151 | 2628.0006 | 209 | 73 | 88
Aug 25, 2011 | 2421:00
Aug 25, 2011 | 2422:00 | 2.132 | 0.62385 | 1.5082 | 76.1 | 54 | 153 | 2987.334 | 209 | 72 | 87
Aug 25, 2011 | 2423:00
Aug 26, 2011 | 2400:00 | 2.157 | 0.64167 | 1.5153 | 72.5 | 54 | 153 | 3016.5007 | 209 | 72 | 87
Aug 26, 2011 | 2401:00
Aug 26, 2011 | 2402:00 | 2.239 | 0.64167 | 1.5973 | 66.8 | 53 | 153 | 3112.1674 | 209 | 71 | 86
Aug 26, 2011 | 2403:00
Aug 26, 2011 | 2404:00 | 2.277 | 0.64167 | 1.6353 | 63 | 49 | 152 | 3156.5008 | 209 | 68 | 83
Aug 26, 2011 | 2405:00
Aug 26, 2011 | 2406:00 | 2.305 | 0.64167 | 1.6633 | 61.6 | 48 | 153 | 3189.1674 | 209 | 68 | 83
Aug 26, 2011 | 2407:00
Aug 26, 2011 | 2408:00 | 2.122 | 0.64167 | 1.4803 | 83 | 58 | 154 | 2975.6674 | 209 | 72 | 87
Aug 26, 2011 | 2409:00
Aug 26, 2011 | 2410:00 | 1.614 | 0.64167 | 0.97233 | 96 | 65 | 151 | 2383.0005 | 209 | 73 | 88
Aug 26, 2011 | 2411:00
Aug 26, 2011 | 2412:00 | 1.573 | 0.64167 | 0.93133 | 100 | 68 | 149 | 2335.1672 | 209 | 74 | 89
Aug 26, 2011 | 2413:00
Aug 26, 2011 | 2414:00 | 1.553 | 0.64167 | 0.91133 | 103 | 69 | 146 | 2311.8339 | 209 | 74 | 88
Aug 26, 2011 | 2415:00
Aug 26, 2011 | 2416:00 | 1.538 | 0.64167 | 0.89633 | Not Recorded | Not Recorded | 145 | 2294.3338 | 209 | 75 | 88
Aug 26, 2011 | 2417:00
Aug 26, 2011 | 2418:00 | 1.618 | 0.64167 | 0.97633 | Not Recorded | Not Recorded | 146 | 2387.6672 | 209 | 75 | 89
Aug 26, 2011 | 2419:00
Aug 26, 2011 | 2420:00 | 1.741 | 0.64167 | 1.0993 | 83.5 | 59 | 148 | 2531.1672 | 209 | 74 | 88
Aug 26, 2011 | 2421:00
Aug 26, 2011 | 2422:00 | 2.056 | 0.64167 | 1.4143 | 80.1 | 54 | 153 | 2898.6674 | 209 | 73 | 88
Aug 26, 2011 | 2423:00
Aug 27, 2011 | 2400:00 | 1.909 | 0.64167 | 1.2673 | 75 | 54 | 152 | 2727.1673 | 209 | 73 | 88
Aug 27, 2011 | 2401:00
Aug 27, 2011 | 2402:00 | 2.172 | 0.64167 | 1.5303 | 67 | 54 | 152 | 3034.0007 | 209 | 70 | 85
Aug 27, 2011 | 2403:00
Aug 27, 2011 | 2404:00 | 2.166 | 0.64167 | 1.5243 | 68.6 | 53 | 154 | 3027.0007 | 209 | 71 | 86
Aug 27, 2011 | 2405:00
Aug 27, 2011 | 2406:00 | 2.212 | 0.64167 | 1.5703 | 65 | 53 | 153 | 3080.6674 | 209 | 70 | 85
Aug 27, 2011 | 2407:00
Aug 27, 2011 | 2408:00 | 2.117 | 0.64167 | 1.4753 | 77 | 68 | 154 | 2969.834 | 209 | 73 | 88
Aug 27, 2011 | 2409:00
Aug 27, 2011 | 2410:00 | 1.569 | 0.64167 | 0.92733 | 84 | 73 | 150 | 2330.5005 | 209 | 75 | 89
Aug 27, 2011 | 2411:00
Aug 27, 2011 | 2412:00 | 1.639 | 0.64167 | 0.99733 | 89 | 74 | 148 | 2412.1672 | 209 | 74 | 88
Aug 27, 2011 | 2413:00
Aug 27, 2011 | 2414:00 | 1.642 | 0.64167 | 1.0003 | 95 | 74 | 147 | 2415.6672 | 209 | 75 | 89
Aug 27, 2011 | 2415:00
Aug 27, 2011 | 2416:00 | 1.451 | 0.64167 | 0.80933 | 91 | 69 | 144 | 2192.8338 | 209 | 76 | 89
Aug 27, 2011 | 2417:00
Aug 27, 2011 | 2418:00 | 1.245 | 0.64167 | 0.60333 | 88 | 67 | 141 | 1952.5004 | 209 | 77 | 90
Aug 27, 2011 | 2419:00
Aug 27, 2011 | 2420:00 | 1.51 | 0.64167 | 0.86833 | 80.5 | 64 | 144 | 2261.6672 | 209 | 75 | 89
Aug 27, 2011 | 2421:00
Aug 27, 2011 | 2422:00 | 1.58 | 0.64167 | 0.93833 | 78 | 62 | 144 | 2343.3339 | 209 | 75 | 88
Aug 27, 2011 | 2423:00
Aug 28, 2011 | 2400:00 | 1.741 | 0.62697 | 1.114 | 70.9 | 59 | 147 | 2531.1672 | 209 | 74 | 88
Aug 28, 2011 | 2401:00
Aug 28, 2011 | 2402:00 | 2.104 | 0.62697 | 1.477 | 65 | 54 | 153 | 2954.6674 | 209 | 71 | 87
Aug 28, 2011 | 2403:00
Aug 28, 2011 | 2404:00 | 2.204 | 0.62697 | 1.577 | 61.9 | 54 | 135 | 3071.3341 | 209 | 63 | 73
Aug 28, 2011 | 2405:00
Aug 28, 2011 | 2406:00 | 2.19 | 0.62697 | 1.563 | 61.7 | 53 | 154 | 3055.0007 | 209 | 71 | 86
Aug 28, 2011 | 2407:00
Aug 28, 2011 | 2408:00 | 1.855 | 0.62697 | 1.228 | 77 | 62 | 151 | 2664.1673 | 209 | 74 | 89
Aug 28, 2011 | 2409:00
Aug 28, 2011 | 2410:00 | 1.554 | 0.62697 | 0.92703 | 85 | 65 | 148 | 2313.0005 | 209 | 75 | 89
Aug 28, 2011 | 2411:00
Aug 28, 2011 | 2412:00 | 1.554 | 0.62697 | 0.92703 | 94 | 72 | 145 | 2313.0005 | 209 | 76 | 90
Aug 28, 2011 | 2413:00
Aug 28, 2011 | 2414:00 | 1.48 | 0.62697 | 0.85303 | 89 | 72 | 142 | 2226.6672 | 209 | 76 | 89
Aug 28, 2011 | 2415:00
Aug 28, 2011 | 2416:00 | 1.566 | 0.62697 | 0.93903 | 72 | 68 | 148 | 2327.0005 | 209 | 75 | 88
Aug 28, 2011 | 2417:00
Aug 28, 2011 | 2418:00 | 1.616 | 0.62697 | 0.98903 | 80 | 64 | 146 | 2385.3339 | 209 | 75 | 89
Aug 28, 2011 | 2419:00
Aug 28, 2011 | 2420:00 | 1.668 | 0.62697 | 1.041 | 72 | 59 | 147 | 2446.0006 | 209 | 73 | 87
Aug 28, 2011 | 2421:00
Aug 28, 2011 | 2422:00 | 1.833 | 0.62697 | 1.206 | 65.5 | 57 | 149 | 2638.5006 | 209 | 73 | 87
Aug 28, 2011 | 2423:00
Aug 29, 2011 | 2400:00 | 2.07 | 0.64167 | 1.4283 | 63.7 | 54 | 153 | 2915.0007 | 209 | 72 | 87
Aug 29, 2011 | 2401:00
Aug 29, 2011 | 2402:00 | 2.166 | 0.64167 | 1.5243 | 60.5 | 52 | 154 | 3027.0007 | 209 | 71 | 86
Aug 29, 2011 | 2403:00
Aug 29, 2011 | 2404:00 | 2.246 | 0.64167 | 1.6043 | 57.1 | 48 | 153 | 3120.3341 | 209 | 69 | 84
Aug 29, 2011 | 2405:00
Aug 29, 2011 | 2406:00 | 2.389 | 0.64167 | 1.7473 | 56 | 44 | 153 | 3287.1675 | 209 | 66 | 82
Aug 29, 2011 | 2407:00
Aug 29, 2011 | 2408:00 | 2.135 | 0.64167 | 1.4933 | 76 | 58 | 154 | 2990.834 | 209 | 72 | 87
Aug 29, 2011 | 2409:00
Aug 29, 2011 | 2410:00 | 1.751 | 0.64167 | 1.1093 | 85 | 64 | 149 | 2542.8339 | 209 | 74 | 89
Aug 29, 2011 | 2411:00
Aug 29, 2011 | 2412:00 | 2.127 | 0.64167 | 1.4853 | 97 | 64 | 154 | 2981.5007 | 209 | 72 | 87
Aug 29, 2011 | 2413:00
Aug 29, 2011 | 2414:00 | 1.949 | 0.64167 | 1.3073 | 96 | 62 | 151 | 2773.834 | 209 | 72 | 87
Aug 29, 2011 | 2415:00
Aug 29, 2011 | 2416:00 | 1.906 | 0.64167 | 1.2643 | 94 | 62 | 152 | 2723.6673 | 209 | 73 | 88
Aug 29, 2011 | 2417:00
Aug 29, 2011 | 2418:00 | 1.954 | 0.64167 | 1.3123 | 89 | 60 | 151 | 2779.6673 | 209 | 73 | 88
Aug 29, 2011 | 2419:00
Aug 29, 2011 | 2420:00 | 2.069 | 0.64167 | 1.4273 | 78 | 57 | 152 | 2913.834 | 209 | 71 | 86
Aug 29, 2011 | 2421:00
Aug 29, 2011 | 2422:00 | 2.215 | 0.64167 | 1.5733 | 73.6 | 54 | 153 | 3084.1674 | 209 | 68 | 84
Aug 29, 2011 | 2423:00
Aug 30, 2011 | 2400:00 | 2.349 | 0.64167 | 1.7073 | 64.1 | 50 | 153 | 3240.5008 | 209 | 67 | 82
Aug 30, 2011 | 2401:00
Aug 30, 2011 | 2402:00 | 2.476 | 0.64167 | 1.8343 | 59 | 45 | 152 | 3388.6675 | 209 | 64 | 80
Aug 30, 2011 | 2403:00
Aug 30, 2011 | 2404:00 | 2.437 | 0.64167 | 1.7953 | 58 | 45 | 152 | 3343.1675 | 209 | 65 | 80
Aug 30, 2011 | 2405:00
Aug 30, 2011 | 2406:00 | 2.502 | 0.64167 | 1.8603 | 53.3 | 40 | 151 | 3419.0008 | 209 | 64 | 79
Aug 30, 2011 | 2407:00
Aug 30, 2011 | 2408:00 | 2.309 | 0.64167 | 1.6673 | 77 | 54 | 151 | 3193.8341 | 209 | 65 | 80
Aug 30, 2011 | 2409:00
Aug 30, 2011 | 2410:00 | 2.1 | 0.64167 | 1.4583 | 86 | 61 | 153 | 2950.0007 | 209 | 70 | 85
Aug 30, 2011 | 2411:00
Aug 30, 2011 | 2412:00 | 2.11 | 0.64167 | 1.4683 | 94 | 70 | 153 | 2961.6674 | 209 | 72 | 87
Aug 30, 2011 | 2413:00
Aug 30, 2011 | 2414:00 | 1.963 | 0.64167 | 1.3213 | 95 | 70 | 152 | 2790.1673 | 209 | 73 | 88
Aug 30, 2011 | 2415:00
Aug 30, 2011 | 2416:00 | 1.856 | 0.64167 | 1.2143 | 93 | 70 | 150 | 2665.334 | 209 | 74 | 88
Aug 30, 2011 | 2417:00
Aug 30, 2011 | 2418:00 | 0.993 | 0.64167 | 0.35133 | 89 | 65 | 136 | 1658.5003 | 209 | 78 | 90
Aug 30, 2011 | 2419:00
Aug 30, 2011 | 2420:00 | 1.31 | 0.64167 | 0.66833 | 79.6 | 60 | 141 | 2028.3338 | 209 | 76 | 89
Aug 30, 2011 | 2421:00
Aug 30, 2011 | 2422:00 | 1.536 | 0.64167 | 0.89433 | 76 | 54 | 143 | 2292.0005 | 209 | 73 | 87
Aug 30, 2011 | 2423:00
Aug 31, 2011 | 2400:00 | 1.969 | 0.61271 | 1.3563 | 68 | 49 | 149 | 2797.1673 | 209 | 71 | 86
Aug 31, 2011 | 2401:00
Aug 31, 2011 | 2402:00 | 2.193 | 0.61271 | 1.5803 | 60 | 46 | 152 | 3058.5007 | 209 | 69 | 84
Aug 31, 2011 | 2403:00
Aug 31, 2011 | 2404:00 | 2.052 | 0.61271 | 1.4393 | 57 | 44 | 152 | 2894.0007 | 209 | 71 | 86
Aug 31, 2011 | 2405:00
Aug 31, 2011 | 2406:00 | 2.173 | 0.61271 | 1.5603 | 54.4 | 40 | 152 | 3035.1674 | 209 | 68 | 84
Aug 31, 2011 | 2407:00
Aug 31, 2011 | 2408:00 | 2.015 | 0.61271 | 1.4023 | 63 | 50 | 152 | 2850.834 | 209 | 70 | 85
Aug 31, 2011 | 2409:00
Aug 31, 2011 | 2410:00 | 1.505 | 0.61271 | 0.89229 | Not Recorded | Not Recorded | Not Recorded | 2255.8338 | Not Recorded | Not Recorded | Not Recorded
Aug 31, 2011 | 2411:00
Aug 31, 2011 | 2412:00 | 1.519 | 0.61271 | 0.90629 | Not Recorded | Not Recorded | Not Recorded | 2272.1672 | Not Recorded | Not Recorded | Not Recorded
Aug 31, 2011 | 2413:00
Aug 31, 2011 | 2414:00 | 1.499 | 0.61271 | 0.88629 | 90 | 68 | 145 | 2248.8338 | 209 | 75 | 89
Aug 31, 2011 | 2415:00
Aug 31, 2011 | 2416:00 | 1.481 | 0.61271 | 0.86829 | 83 | 65 | 144 | 2227.8338 | 209 | 75 | 89
Aug 31, 2011 | 2417:00
Aug 31, 2011 | 2418:00 | 1.522 | 0.61271 | 0.90929 | 83 | 64 | 144 | 2275.6672 | 209 | 74 | 89
Aug 31, 2011 | 2419:00
Aug 31, 2011 | 2420:00 | 1.632 | 0.61271 | 1.0193 | 72.5 | 54 | 146 | 2404.0005 | 209 | 72 | 87
Aug 31, 2011 | 2421:00
Aug 31, 2011 | 2422:00 | 1.901 | 0.61271 | 1.2883 | 63.9 | 50 | 150 | 2717.834 | 209 | 71 | 86
Aug 31, 2011 | 2423:00
Aug 31, 2011 | 0:00 | 2.037 | 0.61271 | 1.4243 | 61.7 | 46 | 151 | 2876.5007 | 209 | 71 | 86